CAT5e POLY JACKET

# WBT Unshielded Four Twisted Pair

# Enhanced Category 5e Horizontal Cable

Extended Testing to 350 MHz

With Messenger

Construction Details:

## No. 24 AWG copper conductor insulated with

polyethylene. Two colored mated insulated conductors twisted

together to form a pair and four pairs assembled

to form a core.  Water block tape wrapped over the core

with a polyethylene jacket with messenger in a siamese construction.

Color Code:

| ### Pair | Primary 1 | Primary 2 |
| --- | --- | --- |
| 1 | White/Blue | ###### Blue |
| 2 | White/Orange | Orange |
| 3 | White/Green | Green |
| 4 | White/Brown | Brown |

Standards:						Applications:

## ANSI/TIA/EIA 568B.2 Category 5e			Supports all category 5 applications including

Swept to 350 MHz					Ethernet 100BASE-TX, 100BASE-VG and 155

ATM.  Particularly suited for high bandwidth

##### applications such as 622 ATM, Wideband, and

Ethernet 1000BASE-T.

Environmental Characteristics:

## Temperature Rating:

- Installation:  	0C to 50C

- Operation: 	-60C to 60C

Maximum installing tension:	25 lb

Nominal cable weight:	40 lb/1000 feet

Nominal cable diameter:	Minor: 0.200 inch

Major: 0.320 inch (.045 galvanized steel messenger)

Electrical Parameters:

## Mutual Capacitance:	14 pF/ft nominal		Max. Conductor D.C.R.:	28.6 ohm/1000 feet

## Capacitance Unbalance:	330 pF/ft maximum	Max. DCR Unbalance:	3%

Velocity of Propagation:	70% 			Max. Delay Skew:		15.0ns/100m

Max. Propagation Delay Skew: 5.7 ns/100m

Characteristic Impedance:

from 0.772 – 100 MHz	100  15%

from 100 MHz – 200 MHz	100  22%

from 200 MHz – 350 MHz	100  32%

CAT5e POLY JACKET

# WBT Unshielded Four Twisted Pair

# Category 5e Horizontal Cable

Extended Testing to 350 MHz

With Messenger

Electrical Characteristics:

| Frequency | SRL | Return Loss | Attenuation | NEXT | PS-NEXT | ELFEXT | PS-ELFEXT |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | dB | dB | dB(100m) | dB | dB | dB | dB |
| MHz | Minimum | Minimum | Maximum | Minimum | Minimum | Minimum | Minimum |
| 1 | 23.0 | 20.0 | 2.0 | 70.3 | 68.3 | 63.8 | 60.8 |
| 4 | 23.0 | 20.3 | 4.0 | 61.3 | 59.3 | 51.7 | 48.7 |
| 10 | 23.0 | 25.0 | 6.4 | 55.3 | 53.3 | 43.8 | 40.8 |
| 16 | 23.0 | 25.0 | 8.2 | 52.3 | 50.3 | 39.7 | 36.7 |
| 20 | 23.0 | 25.0 | 9.2 | 50.8 | 48.8 | 37.7 | 34.7 |
| 31.25 | 21.1 | 23.6 | 11.7 | 47.9 | 45.9 | 33.9 | 30.9 |
| 62.5 | 18.1 | 21.5 | 16.9 | 43.4 | 41.4 | 27.8 | 24.8 |
| 100 | 16.0 | 20.1 | 21.9 | 40.3 | 38.3 | 23.8 | 20.8 |
| 250 | 12.0 | 17.3 | 36.8 | 34.3 | 32.3 | 15.8 | 12.8 |
| 300 | 11.2 | 16.8 | 40.9 | 33.2 | 31.2 | 14.2 | 11.2 |
| 350 | 10.6 | 16.3 | 44.8 | 32.2 | 30.2 | 12.9 | 9.9 |